## U&f Protections-POI@150kV
| Power transformer |  | HV | MV1 | MV2
| Definition (name) | - |  |  |  | e.g. ΜΣ1
| Vector group | -
| Rated maximum apparent power, HV:(MV1-MV2) | MVA |  |  |  | write the MV2 [MVA] only for 3-windings T/Fs
| Rated voltages, HV:(MV1-MV2) | kV | 150 |  |  | write the MV2 [kV] only for 3-windings T/Fs
A: | Transformer HV side |  | Grey cells: fill in only if applicable |  |  | Implemented; Not Implemented
| Definition (name) | - |  |  |  | e.g. P15
| Positon of the connected VTs - HV side | - |  |  |  | 1) upwards of the HV CB; 2) downwards of the HV CB; 3) at HV busbars
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV | 150
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to voltage type
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
B1: | Transformer MV side - TM (MV1 side - TM1 for 2-w TFs) |  | Grey cells: fill in only if applicable
| Definition (name) | - |  |  |  | e.g. P215
| Positon of the connected VTs - MV side | - |  |  |  | 1) at TM (T/F side); 2) at TM (busbars side); 3) at MM (busbars); 4) not connected
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
B2: | Transformer MV2 side - TM2 (for 3-w TFs only) |  | Grey cells: fill in only if applicable
| Definition (name) | - |  |  |  | e.g. P225
| Positon of the connected VTs - MV side | - |  |  |  | 1) at TM (T/F side); 2) at TM (busbars side); 3) at MM (busbars); 4) not connected
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
C: | MV feeder(s) - IPPM(s) |  | Grey cells: fill in only if applicable |  |  | in case there are multiple IPPMs with different V,f settings, please fill in all the individual IPPM settings (add table C at the end)
| Definition (name) | - |  |  |  | e.g. P210 or multiple IPPM names with the same settings
| Positon of the connected VTs - MV side | - |  |  |  | 1) at IPPM (cable side); 2) at IPPM (busbars side); 3) at MM (busbars); 4) not connected
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
D1: | MV interconnection switchboard (from IPPMs) |  | Grey cells: fill in only if applicable |  |  | in case there are multiple MV interconnection switchboards with different V,f settings, please fill in (add table D1 at the end.)
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
D2: | MV interconnection (KIOSK) |  | Grey cells: fill in only if applicable |  |  | in case there are multiple MV RES Kiosks with different V,f settings, please fill in (add table D2 at the end)
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
E: | RES generating units (PV inverters / Wind Generators) or Electricity Storage Converters |  | Grey cells: fill in only if applicable |  |  | in case there are different V,f settings between RES generating units, please fill in (add table E at the end)
| Operating-nominal voltage | V
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | V |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | V |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
If there are [MV feeder(s) - IPPM(s)], [MV interconnection switchboard (from IPPMs)], [RES interconnection (KIOSK)] or [RES generating units or Electricity Storage Converters]
with other settings than above, please fill in respectively new tables C, D1, D2, and E below:
C: | MV feeder(s) - IPPM(s) #2 |  | Grey cells: fill in only if applicable
| Definition (name) | - |  |  |  | e.g. P210 or multiple IPPM names with the same settings
| Positon of the connected VTs - MV side | - |  |  |  | 1) at IPPM (cable side); 2) at IPPM (busbars side); 3) at MM (busbars); 4) not connected
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
D1: | MV interconnection switchboard #2 (from IPPMs #2) |  | Grey cells: fill in only if applicable
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
D2: | MV interconnection (KIOSK #2) |  | Grey cells: fill in only if applicable
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
E: | RES generating units (PV inverters / Wind Generators) or Electricity Storage Converters #2 |  | Grey cells: fill in only if applicable
| Operating-nominal voltage | V
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | V |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | V |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
Repeate if it is necessary.
ΠΡΟΣΟΧΗ: Η τάση αντιστοιχεί στο Σημείο Διασύνδεσης του Σταθμού με το Σύστημα.
ATTENTION: The voltage is at the Point Of Interconnection of the RES with the System.

## U&f Protections-POI@400kV
| Power transformer |  | HV | MV1 | MV2
| Definition (name) | - |  |  |  | e.g. ΜΣ1
| Vector group | -
| Rated maximum apparent power, HV:(MV1-MV2) | MVA |  |  |  | write the MV2 [MVA] only for 3-windings T/Fs
| Rated voltages, HV:(MV1-MV2) | kV | 400 |  |  | write the MV2 [kV] only for 3-windings T/Fs
A: | Transformer HV side |  | Grey cells: fill in only if applicable |  |  | Implemented; Not Implemented
| Definition (name) | - |  |  |  | e.g. P815
| Positon of the connected VTs - HV side | - |  |  |  | 1) upwards of the HV CB; 2) downwards of the HV CB; 3) at HV busbars
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV | 400
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to voltage type
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
B1: | Transformer MV side - TM (MV1 side - TM1 for 3-w TFs) |  | Grey cells: fill in only if applicable
| Definition (name) | - |  |  |  | e.g. P215
| Positon of the connected VTs - MV side | - |  |  |  | 1) at TM (T/F side); 2) at TM (busbars side); 3) at MM (busbars); 4) not connected
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
B2: | Transformer MV2 side - TM2 (for 3-w TFs only) |  | Grey cells: fill in only if applicable
| Definition (name) | - |  |  |  | e.g. P225
| Positon of the connected VTs - MV side | - |  |  |  | 1) at TM (T/F side); 2) at TM (busbars side); 3) at MM (busbars); 4) not connected
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
C: | MV feeder(s) - IPPM(s) |  | Grey cells: fill in only if applicable |  |  | in case there are multiple IPPMs with different V,f settings, please fill in all the individual IPPM settings (add table C at the end)
| Definition (name) | - |  |  |  | e.g. P210 or multiple IPPM names with the same settings
| Positon of the connected VTs - MV side | - |  |  |  | 1) at IPPM (cable side); 2) at IPPM (busbars side); 3) at MM (busbars); 4) not connected
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
D1: | MV interconnection switchboard (from IPPMs) |  | Grey cells: fill in only if applicable |  |  | in case there are multiple MV interconnection switchboards with different V,f settings, please fill in (add table D1 at the end.)
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
D2: | MV interconnection (KIOSK) |  | Grey cells: fill in only if applicable |  |  | in case there are multiple MV RES Kiosks with different V,f settings, please fill in (add table D2 at the end)
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
E: | RES generating units (PV inverters / Wind Generators) or Electricity Storage Converters |  | Grey cells: fill in only if applicable |  |  | in case there are different V,f settings between RES generating units, please fill in (add table E at the end)
| Operating-nominal voltage | V
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | V |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | V |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
If there are [MV feeder(s) - IPPM(s)], [MV interconnection switchboard (from IPPMs)], [RES interconnection (KIOSK)] or [RES generating units or Electricity Storage Converters]
with other settings than above, please fill in respectively new tables C, D1, D2, and E below:
C: | MV feeder(s) - IPPM(s) #2 |  | Grey cells: fill in only if applicable
| Definition (name) | - |  |  |  | e.g. P210 or multiple IPPM names with the same settings
| Positon of the connected VTs - MV side | - |  |  |  | 1) at IPPM (cable side); 2) at IPPM (busbars side); 3) at MM (busbars); 4) not connected
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
D1: | MV interconnection switchboard #2 (from IPPMs #2) |  | Grey cells: fill in only if applicable
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
D2: | MV interconnection (KIOSK #2) |  | Grey cells: fill in only if applicable
| VT_primary:VT_secondary | V |  |  |  | write 0 if not connected
| Operating-nominal voltage | kV
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | kV |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
E: | RES generating units (PV inverters / Wind Generators) or Electricity Storage Converters #2 |  | Grey cells: fill in only if applicable
| Operating-nominal voltage | V
| Phase overvoltage (59) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | V |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s
| Phase undervoltage (27) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Voltage type | - |  |  |  | 1) L-L; 2) L-N; 3) positive sequence
| Operation logic | - |  |  |  | 1) 1-out of-3; 2) 2-out of-3; 3) 3-out of-3
| Setting (primary value) | V |  |  |  | ph-ph or ph-N values according to operating voltage
| Setting (per unit value) | p.u. |  |  |  | per unit on operating-nominal voltage
| Time Delay | s |  |  |  | the settings should not negate the FRT requirements
| Overfrequency (81O) |  | Stage 1 (>) | Stage 2 (>>) | Stage 3 (>>>)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Underfrequency (81U) |  | Stage 1 (<) | Stage 2 (<<) | Stage 3 (<<<)
| Setting | Hz |  |  |  | nominal frequency= 50 Hz
| Time Delay | s
| Automatic Reconnection after Grid recovery |  |  |  |  | Yes; No;
| Grid reconnection recovery time | min |  |  |  | time for reconnection after which the power grid recovers
Repeate if it is necessary.
ΠΡΟΣΟΧΗ: Η τάση αντιστοιχεί στο Σημείο Διασύνδεσης του Σταθμού με το Σύστημα.
ATTENTION: The voltage is at the Point Of Interconnection of the RES with the System.

## LIST (hidden)
SHEET: OC Protections | SHEET: OC Protections | SHEET: U & f Protections
O/C PROTECTION CURVES | T/F GROUNDING - HV SIDE | PROTECTION FUNCTION IMPLEMENTION
Definite Time (DT) | 1) unground (T/F HV windings=D) | Enabled | 1) unground (T/F HV windings=D); 2) unground wye node (T/F HV windings=YN or Y); 3) ground wye node through SVL (T/F HV windings=YN); 4) direct ground of wye node (T/F HV windings=YN)
IEC Normal Inverse (Type A) | 2) unground wye node (T/F HV windings=YN or Y) | Disabled
IEC Very Inverse (Type B) | 3) ground wye node through SVL (T/F HV windings=YN) | VOLTAGE PROTECTION - OPERATING VOLTAGE
IEC Extremely Inverse (Type C) | 4) direct ground of wye node (T/F HV windings=YN) | 1) L-L
IEC Short Time Inverse | T/F GROUNDING - MV SIDE | 2) L-N
IEC Long Time Inverse | 1) ground wye node through resistance (T/F MV windings=yn) | 3) positive sequence | 1) ground wye node through resistance (T/F MV windings=yn); 3) ground through zig-zag shunt ZN (T/F MV windings=d); 4) ground through zig-zag transf. ZNyn (T/F MV windings=d)
UK Long Time Inverse | 2) ground zig-zag node through resistance (T/F MV windings=zn) | VOLTAGE PROTECTION - OPERATING LOGIC
UK Rectifier | 3) ground through zig-zag shunt ZN (T/F MV windings=d) | 1) 1-out of-3
RI type | 4) ground through zig-zag transf. ZNyn (T/F MV windings=d) | 2) 2-out of-3
RD type | PROTECTION FUNCTION IMPLEMENTION | 3) 3-out of-3
ANSI Normal Inverse | Enabled | VOLTAGE PROTECTION - HV SIDE - POSITION OF CONNECTED VTs
ANSI Very Inverse | Disabled | 1) upwards of the HV CB
ANSI Extremely Inverse | T/F WINDINGS NUMBER | 2) downwards of the HV CB
ANSI Moderately Inverse | 2-windings | 3) at HV busbars
ANSI Short Time Inverse | 3-windings | TM VOLTAGE PROTECTION - MV SIDE - POSITION OF CONNECTED VTs
ANSI Long Time Inverse | DIFFERENTIAL PROTECTION (87T) - HV SIDE - POSITION OF CONNECTED CTs | 1) at TM (T/F side)
ANSI Long Time Very Inverse | 1) upwards of the HV CB | 2) at TM (busbars side) | 1) at IPPM (cable side); 2) at IPPM (busbars side); 3) at MM (busbars); 4) not connected
ANSI Long Time Extremely Inverse | 2) downwards of the HV CB | 3) at MM (busbars)
ANSI Definite Inverse | 3) at T/F HV bushings | 4) not connected
| DIFFERENTIAL PROTECTION (87T) - MV SIDE - POSITION OF CONNECTED CTs | IPPM VOLTAGE PROTECTION - MV SIDE - POSITION OF CONNECTED VTs
| 1) at TM (T/F side) | 1) at IPPM (cable side)
| 2) at TM (MV busbars side) | 2) at IPPM (busbars side)
| 3) at IPPMs entarance (wide zone differential) | 3) at MM (busbars)
| S/S GROUNDING NODE - POSITION OF CONNECTED CT | 4) not connected
1) T/F N node at HV side
2) T/F N node MV side
3) Grounding T/F N node
4) not connected
BACKUP O/C PROTECTION - HV SIDE - POSITION OF CONNECTED VTs
1) upwards of the HV CB
2) downwards of the HV CB
3) at HV busbars
DIRECTION OF O/C ELEMENTS - GENERAL
1) Non-directional
2) Forward
3) Reverse
T/F REF PROTECTION (87N) - IMPLEMENTATION EQUIPMENT
1) in T/F main differential relay (A)
2) in HV side backup relay (B)
3) in MV side main relay (E)
4) not implemented
T/F REF (87N) PROTECTION - PHASES A, B, C - POSITION OF CONNECTED CTS
1) upwards of the HV CB
2) downwards of the HV CB
3) at T/F HV bushings
4) at T/F MV bushings
5) at TM (T/F side)
6) at TM (MV busbars side)
TM O/C PROTECTION - MV SIDE - POSITION OF CONNECTED CTs
1) at TM (T/F side)
2) at TM (MV busbars side)
TM O/C PROTECTION - MV SIDE - POSITION OF CONNECTED VTs
1) at TM (T/F side)
2) at TM (MV busbars side)
3) at MM (MV busbars)
4) not connected
TRIPPING
1) HV
2) TM
3) IPPM
4) HV & TM
5) HV & TM & BSM
6) TM & BSM
7) HV & TM & BSM & IPPMs of the MV bus
8) TM & BSM & IPPMs of the MV bus
9) TM & IPPMs of the MV bus