## demo BESS plant (ESM)
[14 empty] | HV nominal voltge: | 150 | kV
[14 empty] | MV nominal voltge: | 20 | kV
Cable manufacturer
Transfo-Number | Transfo-winding | No. of racks | Rated capacity 1 (kWh) | C-rate 2 | Rated active power charge (kW) 3 | Rated active power discharge (kW) 3 | Auxiliaries (kW) 4 | Auxiliaries (kVAr) 4 | No. of converters | Converter (kVA) | From | To | length (km) | Type of conductor | Rdc (Ω/km) | R+ (Ω/km) | X+ (Ω/km) | C+ (μF/km) | R0 (Ω/km) | X0 (Ω/km) | C0 (μF/km) | Imax (A)
TR-1 | 1 | 2 | 7200 | 0.5 | 3600 | 3600 | 0 | 0 | 1 | 3600 | Tr-1 | JB1 | L1 | XLPE A2XS2Y 3x(1x300mm2) | 0.1 | 0.13 | 0.109 | 0.249 | 0.942 | 0.061 | 0.249 | 414
TR-1a | 1 | 0 | 0 |  | 0 | 0 | 50 | 28 |  |  | Tr-3 | JB1 | L2 | XLPE A2XS2Y 3x(1x300mm2) | 0.1 | 0.13 | 0.109 | 0.249 | 0.942 | 0.061 | 0.249 | 414
TR-3 | 1 | 2 | 4000 | 0.5 | 2000 | 2000 | 0 | 0 | 1 | 2000 | Tr-4 | JB1 | L3 | XLPE A2XS2Y 3x(1x400mm2) | 0.0778 | 0.102 | 0.104 | 0.273 | 0.869 | 0.057 | 0.273 | 470
| 2 | 0 | 0 |  | 0 | 0 | 90 | 50 |  |  | Tr-4 | JB1 | L4 | XLPE A2XS2Y 3x(1x400mm2) | 0.0778 | 0.102 | 0.104 | 0.273 | 0.869 | 0.057 | 0.273 | 470
TR-4 | 1 | 4 | 7000 | 0.5 | 3500 | 3500 | 0 | 0 | 2 | 3600 | Tr-6 | JB1 | L5 | XLPE A2XS2Y 3x(1x630mm2) | 0.0469 | 0.0626 | 0.097 | 0.33 | 0.738 | 0.05 | 0.33 | 602
TR-4a | 1 | 0 | 0 |  | 0 | 0 | 88 | 49 |  |  | Tr-6 | JB1 | L6 | XLPE A2XS2Y 3x(1x630mm2) | 0.0469 | 0.0626 | 0.097 | 0.33 | 0.738 | 0.05 | 0.33 | 602
TR-6 | 1 | 4 | 6000 | 0.5 | 3000 | 3000 | 0 | 0 | 2 | 3000 | JB1 | MV | L7 | XLPE A2XS2Y 3x(1x800mm2) | 0.0367 | 0.051 | 0.094 | 0.372 | 0.663 | 0.047 | 0.372 | 677
| 2 | 0 | 0 |  | 0 | 0 | 75 | 42 |  |  | JB1 | MV | L8 | XLPE A2XS2Y 3x(1x800mm2) | 0.0367 | 0.051 | 0.094 | 0.372 | 0.663 | 0.047 | 0.372 | 677
Total ESM |  |  | 24200 |  | 12100 | 12100 | 303 | 169 | 6 | 12200 | Cable formation: triangular touching Rdc: max DC Resistance of conductor at 20oC R+: conductor AC resistance (Ω/km) at maximum operating temperature (90oC) X+: inductive reactance (Ω/km) C+: nominal phase capacitance (μF/km) R0: zero phase sequence resistance (Ω/km) X0: zero phase sequence reactance (Ω/km) C0: zero phase sequence capacitance (μF/km) Imax: current carrying capacity of cable Imax conditions: laid directly in ground, load factor: 1.0, triangular touching formation, metallic sheaths solidly-bonded (at both ends), soil thermal resistivity: 1.5 K.m/W, depth of laying: 0.8m, ground temperature: 20oC
1 @rack terminals, BOL, reference environmental conditions 2 C-rate: rate of time to charge to the max depth of charge (DOC) / discharge to the max depth of discharge (DOD), t=1/C-rate (in hours), t=60/C-rate (in min) 3 @converter AC terminal 4 max auxiliary load consumption

## OLTC-AVR
Στοιχεία Συστήματος Αλλαγής Τάσης Υπό Φορτίο (OLTC) του Μ/Σ Ανύψωσης 150kV/ΜΤ
| Υ/Σ | Αριθμός και ισχύς Μ/Σ | AVR-OLTC target voltage (kV) | dead band 1 (± % or ± kV) | time1 (sec) | dead band 2 (± % or ± kV) | time2 (sec) | Περιγραφή
Υπόδειγμα | (Όνομα Υ/Σ) | [1] 40/50 | 20 | ± 1.5% (± 0.3kV) | 60 | ± 3.5% (± 0.7kV) | 1 | AVR target voltage 20kV ΟΡΙΟ 1: ± 1,5% ΟΡΙΟ 2: ± 3,5% Σε αλλαγή τάσης κάτω του ορίου 1 δεν γίνεται αλλαγή. Σε αλλαγή τάσης ανάμεσα στο όριο 1 και 2 γίνεται αλλαγή σε ένα λεπτό Σε αλλαγή τάσης πάνω από το όριο 2 γίνεται αλλαγή αμέσως